Affordable Care Facility Assessment

Additional Services

Electrical/Plumbing Assessment

# PROJECT DETAILS

| Site Number: | 13467 |
| --- | --- |
| Project Type: | Affordable Care Facility Assessment |
| Site Address: | 685 Bloomfield Ave, Suite 103 Verona, NJ 07044 |
| Site Total SF: | 1,111 SF |

# SUMMARY

| - ELECTRICAL ASSESSMENT |  |
| --- | --- |
| - What is the existing electrical load in the lab area? | 9.70 Amps |
| - Is the lab area a dedicated circuit? | Yes |
| - Do all circuits in the lab area have adequate amps is additional equipment requiring 3.8 amps may be installed without overlanding the circuit? If no, please describe | The Lab circuit breaker is rated for 20amps but the lab was only using around 9.70amps so a 3.8 amp equipment can be installed without overloading the circuit. |
| - What is the existing electrical load in the X-Ray area? (Maybe in multiple locations) | 2amps on a 20amp breaker 3amp on a 20amp breaker |
| - Do all circuits in the X-ray area have adequate amps? | Yes. There are 2 separate 20amp breaker for x-ray |
| ▪ Test all existing circuits in the X-Ray area to ensure adequate amps available so that additional equipment requiring 10.8 amps may be installed without overloading the current circuits. - Note: if the lab area circuit is not dedicated to the lab area, please indicate that new dedicated circuit is required. | The X-ray area have adequate amps available for an additional equipment requiring 10.8 amps. It can be installed without overloading the current circuits. |

| - PLUMBING ASSESSMENT |  |
| --- | --- |
| - Provide camera inspection/sewer video inspection of existing sewer system from building to city connection. ▪ If no clean out is located, please remove, and reinstall a toilet or other plumbing fixture as needed to perform the work. | N/A |
| - Is there a clean out located? | N/A |
| - Slope of the waste lines? Is the slope adequate for possible rests room addition or relocation? |  |